## XV3501C
|  |  | 仪表数据表 |  |  | 项目名称 |  | XLP2 PTA 项目
[6 empty] | PROJECT |  | XLP2 PTA PROJECT
|  |  | INSTRUMENT DATA SHEET |  |  | 分项名称 |  | 自控
|  |  | 蝶 阀 |  |  | SUBPROJECT |  | AUTOCONTROL
|  |  | BUTTERFLY VALVE |  |  | 图号DWG.NO.
End User |  |  |  | XIANG LU PETROCHEMICALS (ZHANGZHOU) CO. LTD
Design Institute |  |  |  | SAHNGHAI PENGZHAN BULK SOLID ENGINEERING CO.,LIMITED
Project Name |  |  |  | POWDER PNEUMATIC CONVEYING SYSTEM
General | 1 | Instrument Name | Qty. | Butterfly valve |  |  | 2
| 2 | Tag Number | P&ID No. | XV3501C / XV3502C |  |  | OCS11001.201.3503
| 3 | Installation Area |  | CTA dryer
| 4 | Installation Position
Service Condition | 5 | Fluid | State | OFF GAS |  |  | GAS
| 6 | Design Press. Mpa(G) | Design Temp. ℃ | 0.5 |  |  | 70
| 7 | Oper. Press. Mpa(G) | Oper. Temp. ℃ | 0.3 |  |  | 40
| 8 | Hazardous area classification |  | Class 1 division 2 group D,G
| 9 | Upstream pressure .Mpa | Downstream pressure Mpa
| 10 | Calc.Cv | Relative Travel. %
| 11 | Flow Characteristic | Flow Rate
| 12 | Shut-0ff DP Mpa
Valve Body/Trim Datasheet | 13 | Valve Type |  | Butterfly valve
| 14 | Body Size | Bonnet Type | 8" |  |  | N/A
| 15 | End Connection Type |  | Wafer Type
| 16 | Body/Bonnect Mat'l |  | Ductile iron GGG40
| 17 | Seat Mat'l | Gate Mat'l | EPDM-white |  |  | 321 or equation
| 18 | Stem Mat'l | Packing Mat'l | 304 |  |  | EPDM
| 19 | Port Size | Pressure Rating | Full Port |  |  | ANSI CL150 B16.5
| 20 | Flush Port |  | NO
| 21 | Leakage Class |  | Class VI
Actuator Datasheet | 22 | Actuator Model |  | Double Acting Cylinder
| 23 | Electric/Air Fail Position | Acting mode | EFL AFL |  |  | Double Acting EB6.1-SYD
| 24 | Available Air Supply Press. Mpa(G) |  | 0.45-0.8
| 25 | Full Stroke Time（S） |  | <10 s
| 26 | Volume Tank Air Supply Cycle Times |  | N/A
| 27 | Handwheel & Location |  | N/A
Accessories | 28 | Limit Switch Model/Manufacture |  | Proximity sensors P&F NJ4-12GM-N X2
|  | Rated operating distance | Explosion Proof | 5 mm |  |  | 本安EEX iaIICT6
|  | Conn. Size | Indication of the switching state | 1/2" NPT |  |  | LED,yellow
| 29 | Filter Regulator Model/Manufacture |  | Norgen B73-2GK
| 30 | Air operated valve |  | N/A
| 31 | Solenoid Model/Manufacture |  | Norgren 2636247.4210
|  | Input Singal | Explosion Proof | 24VDC |  |  | EExmdⅡCT6,IP65
|  | Air/Electric Conn. Size | Power/Coils | 1/4" NPT / 1/2" NPT |  |  | 3.9 w /Double Coils
|  | Quick exhaust valve |  | Yes
|  | Terminal box/Internal Wire |  | MSKCEX05 Internel wiring by venderEExdIIBT4
Note：
00 |  | Issue For Quote |  | S.H.F/H.J.Q | F.Y.Z |  | W.Z |  | 2011-05-18
REV. 版次 |  | DESCRIPTION 描述 |  | BY 设计 | CHKD 核对 |  | APVD 批准 |  | DATE 日期